For marine applications using Danfoss IC7-class drives, a continuous VFD cable with 360° bonded shields at both ends is best.

Any VFD cable interruption is treated as an EMC boundary. The motor cable shield is terminated 360° to the disconnect enclosure at entry and exit, and the enclosure is bonded to Permanent Earth with a short, wide connection. The enclosure itself provides shield continuity, preventing high-frequency common-mode currents from coupling into the vessel structure.

Shield handling rules (marine-tailored)

- Treat the disconnect box as an EMC enclosure

Per Danfoss IC7 and ABB marine guidance:

- Any metallic interruption becomes part of the EMC system

- Shield must see metal immediately at entry

Marine rule:

If the VFD cable enters it, the shield bonds to it.

- 360° shield termination at all four boundaries

At each of the following:

- VFD cabinet

- Disconnect box (IN)

- Disconnect box (OUT)

- Motor terminal box

Method

- EMC gland or 360° clamp

- Direct bond to bare metal enclosure wall

- No pigtails

- No terminal-block landings

This aligns with:

- IEC 61800-3 (minimize HF impedance, not DC resistance)

- Danfoss IC7 installation guidance

- ABB marine VFD practices

- The enclosure is the shield bridge

Do not splice the braid end-to-end inside the box.

Correct concept:

- Cable A shield → 360° bonded to box

- Cable B shield → 360° bonded to box

- Box wall provides continuity

This avoids:

- HF loops

- antenna stubs

- unpredictable shield current paths

- Bond the disconnect box to Permanent Earth — the right way

- Use a short, wide braided ground strap

- As straight as possible

- Bond to:

  - the same local Permanent Earth node used by the VFD system

  - not directly to the hull unless that is your defined Permanent Earth reference

Width beats gauge. A 25 mm braided strap outperforms a 2/0 AWG wire at high frequency.

- Keep High Frequency currents out of the hull

In towboats, hull current = noise + corrosion risk.

Therefore:

- Shield → enclosure → Permanent Earth → VFD common-mode network

- Not: Shield → Permanent Earth wire → vessel structure → motor

This is where many “works on land, fails on boats” installs go wrong.

Internal disconnect-box layout (what inspectors never see)

Inside the disconnect box:

- Keep phases tightly bundled

- Route along enclosure wall, not mid-air

- No unnecessary conductor separation

- Minimize lead length from gland to switch

- Every enclosure wall is a 360° shield termination

- The disconnect box is part of the EMC chain, not a break

- PE bonding is short, wide, and local

- No shield currents are forced into the vessel structure

This reduces:

- loop inductance

- radiated magnetic fields

- switching noise inside the box

Do / Do-Not list

Do

- Use EMC-rated glands (not standard strain reliefs)

- Remove paint locally at shield bond points

- Use stainless hardware with serrated washers

- Bond motor frame directly to local structure in addition to Permanent Earth

Do Not

- Float shields at the disconnect

- Pigtail shields to studs

- Assume DC continuity = EMC continuity

- Route VFD power cable parallel to signal/encoder cabling